## Info
Polynomial coefficients, information
This file contains polynomial coefficients for Danfoss Commercial Compressors. The data in this file shall only be used by expert users. Read carefully the instructions below before proceeding.
Data in °C & °F
Page °C gives the coefficients in 'SI'-units (°C, K, W, A, kg, s). These are the official source data.
Page °F gives the coefficients in Imperial units (°F, Btu/h, W, A, lb, s). These are converted data.
Due to rounding of data, very small differences may occur between the calculation results with data on both pages but these differences are usually smaller than 0.1% and much smaller than measurement errors. Danfoss recommends the use of the data on page °C.
Base conditions
Each line of coefficients is valid for a given set of base conditions; RgtBase, ShBase & ScBase. Note that these base conditions can vary between compressors or between frequencies. If calculation data are needed at another base than the given base conditions, the results from the polynomial coeficients shall be recalculated using refrigerant data. In such case it's strongly recommended to use the Danfoss Foresee program or the Danfoss RS+ program instead of the coefficients. Danfoss can not supply you with polynomial coefficients at other base conditions than the given ones.
Operating envelope
Each compressor-refrigerant-frequency combination is subjected to a certain operating envelope which can be found in the Selection and Application guidelines for these compressors. However the envelopes are not included in the polynomial coefficients. In other words, the fact that the coefficients give a result at a certain condition does not automatically mean that this condition is valid. In case of doubt, use the Danfoss Foresee program or the Danfoss RS+ program.
Calculations
As an extra functionality, the sheets have the 10-coefficient-polynomial equations included in the last columns which calculate the performance data for the temperatures in columns T.evap and T.cond. It means that the sheets can be used as a quick calculation tool.
T.evap & T.cond may be modified by the user and the capacity data will change accordingly. However, keep in mind the remarks under 'Operating envelope'.
RGT, SH & SC are copied from RgtBase, ShBase & ScBase. They may never be changed! The capacity data will not change accordingly. See the remarks under 'Base conditions'.
If 2 lines of data have different base conditions, this must be taken into account when comparing calculation results.
Legends
Asercom | Indication whether the data have Asercom certification (- = not Asercom certified, ACP = Asercom certified)
RGT, RgtBase | Return gas temperature or Suction gas temperature (Either RgtBase or ShBase is used.)
SH, ShBase | Superheat (Either RgtBase or ShBase is used.)
SC, ScBase | Subcooling
T. evap | Evaporating temperature or Saturated suction temperature
T. cond | Condensing temperature or Saturated discharge temperature
Danfoss can accept no responsibility for possible errors in catalogues, brochures and other printed material. Danfoss reserves the right to alter its products without notice. This also applies to products already on order provided that such alternations can be made without subsequential changes being necessary in specifications already agreed. All trademarks in this material are property of the respective companies. Danfoss and the Danfoss logotype are trademarks of Danfoss A/S. All rights reserved.

## °C
Model | Drive | Refrigerant | Frequency | Speed | Asercom | RgtBase | ShBase | ScBase | Q0 | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | Q9 | P0 | P1 | P2 | P3 | P4 | P5 | P6 | P7 | P8 | P9 | A0 | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | A9 | version | T. evap | T. cond | RGT | SH | SC | Capacity | Power input | Current | C.O.P. | E.E.R.
|  |  | Hz | rpm |  | °C | K | K | Cooling capacity in W | [9 empty] | Power input in W | [9 empty] | Current consumption in A | [10 empty] | °C | °C | °C | K | K | W | W | A | W/W | Btu/W.h
NTZ048-1 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 12388.0996 | 427.813 | -116.464 | 4.5971 | -3.9918 | -0.43487 | 0.012745 | -0.038795 | -0.0037758 | 0.0025002 | -425.912 | -108.294 | 87.4809 | -2.4667 | 3.1955 | -0.4219 | -0.014269 | 0.02589 | -0.0082034 | -0.00082697 | 11.3477 | 0.30028 | -0.15131 | 0.0064189 | -0.0050506 | 0.0054991 | 5.8187e-05 | -5.5569e-05 | 8.9633e-05 | -3.5097e-05 | 85 70 801 -B | -35 | 40 | 20 | - | 0 | 1204.3197 | 980.0559 | 6.0348 | 1.2288 | 4.194
NTZ048-3 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 12028.2998 | 415.582 | -105.247 | 4.4746 | -3.6994 | -0.56845 | 0.012504 | -0.036872 | -0.0055858 | 0.0030476 | 477.748 | -74.5284 | 39.4516 | -2.0165 | 1.8715 | 0.43006 | -0.012695 | 0.013278 | 2.5182e-05 | -0.0062647 | 7.4658 | 0.19756 | -0.099535 | 0.0042232 | -0.0033229 | 0.0036176 | 3.8284e-05 | -3.6557e-05 | 5.8973e-05 | -2.3088e-05 | 0 | -35 | 40 | 20 | - | 0 | 1189.1139 | 1054.6884 | 3.9705 | 1.1275 | 3.848
NTZ048-4 |  | R404A | 50 | 2900 | ACP | 20 | - | 0 | 10350.7002 | 359.419 | -103.353 | 3.8413 | -3.5932 | -0.27432 | 0.010274 | -0.034568 | -0.0016135 | 0.0016355 | -85.3051 | -75.3121 | 65.0302 | -1.7829 | 2.3271 | -0.19752 | -0.010456 | 0.017323 | -0.0054291 | -0.0019829 | 1.3935 | -0.061056 | 0.063602 | -0.0016012 | 0.0025999 | -4.6038e-06 | -1.1142e-05 | 2.2809e-05 | -3.6345e-06 | -2.9469e-06 | 85 70 609-A | -35 | 40 | 20 | - | 0 | 994.7413 | 868.183 | 2.0762 | 1.1458 | 3.9105
NTZ048-4 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 12028.2998 | 415.582 | -105.247 | 4.4746 | -3.6994 | -0.56845 | 0.012504 | -0.036872 | -0.0055858 | 0.0030476 | 477.748 | -74.5284 | 39.4516 | -2.0165 | 1.8715 | 0.43006 | -0.012695 | 0.013278 | 2.5182e-05 | -0.0062647 | 3.7423 | 0.099028 | -0.049892 | 0.0021169 | -0.0016656 | 0.0018134 | 1.919e-05 | -1.8324e-05 | 2.956e-05 | -1.1573e-05 | 85 70 610-A | -35 | 40 | 20 | - | 0 | 1189.1139 | 1054.6884 | 1.9902 | 1.1275 | 3.848
NTZ048-5 |  | R404A | 50 | 2900 | - | 20 | - | 0 | 10252.0996 | 363.412 | -84.346 | 4.044 | -3.1627 | -0.58925 | 0.010935 | -0.034169 | -0.0058256 | 0.0028649 | 850.155 | -3.2918 | 48.0587 | 0.093672 | 1.3365 | -0.30901 | 0.0046735 | 0.0055177 | -0.0046737 | 0.00011567 | -5.3418 | -0.32278 | 0.70453 | -0.0068541 | 0.013464 | -0.010742 | -3.9253e-05 | 0.00011418 | -6.0198e-05 | 6.3595e-05 | 85 70 798-A | -35 | 40 | 20 | - | 0 | 964.155 | 976.0408 | 4.4215 | 0.98782 | 3.3714
NTZ048-9 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 12028.2998 | 415.582 | -105.247 | 4.4746 | -3.6994 | -0.56845 | 0.012504 | -0.036872 | -0.0055858 | 0.0030476 | 477.748 | -74.5284 | 39.4516 | -2.0165 | 1.8715 | 0.43006 | -0.012695 | 0.013278 | 2.5182e-05 | -0.0062647 | 4.6778 | 0.12379 | -0.062365 | 0.0026461 | -0.002082 | 0.0022667 | 2.3988e-05 | -2.2905e-05 | 3.6951e-05 | -1.4466e-05 | 85 70 835-AE | -35 | 40 | 20 | - | 0 | 1189.1139 | 1054.6884 | 2.4878 | 1.1275 | 3.848
NTZ068-1 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 21610.8008 | 740.482 | -347.061 | 8.917 | -8.7419 | 1.9785 | 0.035499 | -0.064853 | 0.021803 | -0.0058054 | 2600.1399 | 95.1984 | 70.5396 | 1.485 | 0.27891 | -1.0049 | 0.010536 | -0.0033149 | 0.0012467 | 0.0067077 | 8.0767 | -0.10012 | 0.1689 | -0.0040404 | 0.0085921 | 0.00060536 | -2.9585e-05 | 9.2578e-05 | -1.1375e-05 | -1.0964e-05 | 85 70 802-B | -35 | 40 | 20 | - | 0 | 1846.706 | 1656.0596 | 8.0669 | 1.1151 | 3.8059
NTZ068-3 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 20093.1575 | 637.4738 | -278.0328 | 6.5973 | -6.952 | 1.1342 | 0.019497 | -0.054703 | 0.008649 | -0.0034959 | 2458.4119 | 38.0184 | 33.571 | 0.3082 | 0.70256 | 0.19783 | 0.0036785 | 0.0045672 | 0.0077899 | -0.00034937 | 11.2286 | 0.27269 | -0.12481 | 0.0048589 | -0.0043316 | 0.0042574 | 3.87e-05 | -3.2633e-05 | 7.8196e-05 | -2.2166e-05 | 0 | -35 | 40 | 20 | - | 0 | 2065.0985 | 1788.5745 | 6.4643 | 1.1546 | 3.9406
NTZ068-4 |  | R404A | 50 | 2900 | ACP | 20 | - | 0 | 17028.0996 | 540.232 | -235.621 | 5.5909 | -5.8915 | 0.96123 | 0.016523 | -0.046359 | 0.0073297 | -0.0029626 | 2083.3999 | 32.219 | 28.45 | 0.26119 | 0.59539 | 0.16765 | 0.0031174 | 0.0038705 | 0.0066016 | -0.00029608 | 5.941 | 0.14428 | -0.066039 | 0.0025709 | -0.0022918 | 0.0022526 | 2.0476e-05 | -1.7266e-05 | 4.1373e-05 | -1.1728e-05 | 85 70 662-A | -35 | 40 | 20 | - | 0 | 1750.0835 | 1515.7411 | 3.4202 | 1.1546 | 3.9406
NTZ068-4 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 20093.1575 | 637.4738 | -278.0328 | 6.5973 | -6.952 | 1.1342 | 0.019497 | -0.054703 | 0.008649 | -0.0034959 | 2458.4119 | 38.0184 | 33.571 | 0.3082 | 0.70256 | 0.19783 | 0.0036785 | 0.0045672 | 0.0077899 | -0.00034937 | 5.941 | 0.14428 | -0.066039 | 0.0025709 | -0.0022918 | 0.0022526 | 2.0476e-05 | -1.7266e-05 | 4.1373e-05 | -1.1728e-05 | 85 70 583-AE | -35 | 40 | 20 | - | 0 | 2065.0985 | 1788.5745 | 3.4202 | 1.1546 | 3.9406
NTZ068-5 |  | R404A | 50 | 2900 | - | 20 | - | 0 | 16438.5996 | 581.554 | -206.654 | 6.6386 | -6.6409 | 0.53077 | 0.020856 | -0.058725 | 0.0074967 | -0.0023293 | 1545.8101 | -11.275 | 58.795 | -0.72308 | 2.1876 | -0.21574 | -0.0053149 | 0.02358 | -0.0033655 | 0.0010172 | 6.3512 | -0.35276 | 0.24829 | -0.0083565 | 0.018742 | 0.0012921 | -2.2747e-05 | 0.00026744 | -3.2296e-05 | -1.3999e-05 | 85 70 832-A | -35 | 40 | 20 | - | 0 | 1756.1417 | 1635.4903 | 9.214 | 1.0738 | 3.6647
NTZ068-9 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 20093.1575 | 637.4738 | -278.0328 | 6.5973 | -6.952 | 1.1342 | 0.019497 | -0.054703 | 0.008649 | -0.0034959 | 2458.4119 | 38.0184 | 33.571 | 0.3082 | 0.70256 | 0.19783 | 0.0036785 | 0.0045672 | 0.0077899 | -0.00034937 | 7.4857 | 0.18179 | -0.083209 | 0.0032393 | -0.0028877 | 0.0028382 | 2.58e-05 | -2.1756e-05 | 5.213e-05 | -1.4777e-05 | 85 70 836-AE | -35 | 40 | 20 | - | 0 | 2065.0985 | 1788.5745 | 4.3095 | 1.1546 | 3.9406
NTZ096-1 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 21360.3008 | 715.652 | -77.7057 | 8.0054 | -3.2582 | -2.6529 | 0.026696 | -0.043175 | -0.027096 | 0.012842 | -1397.22 | -242.159 | 197.81 | -4.6013 | 7.8773 | -0.39154 | -0.022049 | 0.061255 | -0.01879 | -0.0077372 | 21.8148 | 0.39268 | -0.22794 | 0.0018816 | -0.0083671 | 0.011087 | -2.4604e-06 | -5.2822e-05 | 0.00020719 | -7.5947e-05 | 85 70 803-A | -35 | 40 | 20 | - | 0 | 2406.7296 | 2203.3579 | 11.7656 | 1.0923 | 3.728
NTZ096-3 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 22599.6992 | 759.36 | -135.898 | 8.3948 | -4.7747 | -1.861 | 0.026768 | -0.052367 | -0.016444 | 0.0095436 | -1397.15 | -222.22 | 192.682 | -4.4364 | 6.9609 | -0.66578 | -0.022244 | 0.056812 | -0.01325 | -0.0040744 | 13.1132 | 0.23601 | -0.13692 | 0.0011306 | -0.0050279 | 0.0066637 | -1.4777e-06 | -3.174e-05 | 0.00012455 | -4.5649e-05 | 0 | -35 | 40 | 20 | - | 0 | 2394.7735 | 2061.5153 | 7.0738 | 1.1617 | 3.9647
NTZ096-4 |  | R404A | 50 | 2900 | ACP | 20 | - | 0 | 18767.5 | 708.906 | -70.5356 | 8.9807 | -3.841 | -2.3925 | 0.034295 | -0.047316 | -0.024984 | 0.011041 | -1430.5601 | -149.966 | 213.583 | -2.2891 | 6.7945 | -1.712 | -0.0061073 | 0.050351 | -0.027075 | 0.002851 | 1.8079 | -0.1553 | 0.15462 | -0.0047074 | 0.006366 | -0.00041348 | -3.5109e-05 | 7.1639e-05 | -6.3289e-06 | -2.5656e-06 | 85 70 611-A | -35 | 40 | 20 | - | 0 | 2002.0709 | 1733.5969 | 3.2932 | 1.1549 | 3.9415
NTZ096-4 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 22599.6992 | 759.36 | -135.898 | 8.3948 | -4.7747 | -1.861 | 0.026768 | -0.052367 | -0.016444 | 0.0095436 | -1397.15 | -222.22 | 192.682 | -4.4364 | 6.9609 | -0.66578 | -0.022244 | 0.056812 | -0.01325 | -0.0040744 | 6.1105 | 0.10998 | -0.063802 | 0.00052683 | -0.0023429 | 0.0031052 | -6.886e-07 | -1.4791e-05 | 5.8038e-05 | -2.1272e-05 | 85 70 612-A | -35 | 40 | 20 | - | 0 | 2394.7735 | 2061.5153 | 3.2963 | 1.1617 | 3.9647
NTZ108-1 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 29378.1992 | 1118.86 | -228.331 | 13.1043 | -10.304 | -1.6852 | 0.039626 | -0.11076 | -0.012974 | 0.0061244 | 2248.22 | -9.8783 | 139.84 | -0.59825 | 3.8868 | -0.62763 | -0.00063992 | 0.026499 | -0.0079046 | -0.0017971 | 12.8376 | -0.16963 | 0.44666 | -0.0038211 | 0.019559 | 0.0011483 | 1.9088e-05 | 0.00021585 | -4.6235e-06 | -2.9786e-05 | 85 70 804-A | -35 | 40 | 20 | - | 0 | 2858.9853 | 2662.5341 | 14.5259 | 1.0738 | 3.6648
NTZ108-3 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 28879.4004 | 1101.6899 | -231.848 | 12.9197 | -10.3447 | -1.5293 | 0.03913 | -0.11039 | -0.011034 | 0.0054372 | -879.383 | -144.214 | 271.748 | -3.0309 | 7.3478 | -2.6038 | -0.018331 | 0.053055 | -0.031533 | 0.0079156 | 7.3554 | -0.097163 | 0.25583 | -0.0021887 | 0.011205 | 0.00065904 | 1.0938e-05 | 0.00012366 | -2.6521e-06 | -1.7073e-05 | 0 | -35 | 40 | 20 | - | 0 | 2787.9787 | 2530.2961 | 8.3216 | 1.1018 | 3.7605
NTZ108-4 |  | R404A | 50 | 2900 | ACP | 20 | - | 0 | 24162.5 | 847.772 | -231.68 | 9.566 | -7.9638 | -0.62672 | 0.027552 | -0.081149 | -0.0062128 | 0.0029158 | 1807.53 | -20.0276 | 83.0083 | -0.79443 | 2.1033 | -0.07719 | -0.0017948 | 0.013103 | 0.0046121 | -0.0026453 | 2.3583 | -0.2244 | 0.15544 | -0.005568 | 0.0087303 | 2.3173e-05 | -3.4937e-05 | 9.532e-05 | -2.6058e-05 | -8.1127e-06 | 85 70 663-A | -35 | 40 | 20 | - | 0 | 2465.2469 | 2079.0299 | 4.5325 | 1.1858 | 4.047
NTZ108-4 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 28879.4004 | 1101.6899 | -231.848 | 12.9197 | -10.3447 | -1.5293 | 0.03913 | -0.11039 | -0.011034 | 0.0054372 | -879.383 | -144.214 | 271.748 | -3.0309 | 7.3478 | -2.6038 | -0.018331 | 0.053055 | -0.031533 | 0.0079156 | 3.9802 | -0.052577 | 0.13844 | -0.0011844 | 0.0060633 | 0.00035662 | 5.919e-06 | 6.6914e-05 | -1.4351e-06 | -9.2385e-06 | 85 70 614-A | -35 | 40 | 20 | - | 0 | 2787.9787 | 2530.2961 | 4.503 | 1.1018 | 3.7605
NTZ108-9 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 28879.4004 | 1101.6899 | -231.848 | 12.9197 | -10.3447 | -1.5293 | 0.03913 | -0.11039 | -0.011034 | 0.0054372 | -879.383 | -144.214 | 271.748 | -3.0309 | 7.3478 | -2.6038 | -0.018331 | 0.053055 | -0.031533 | 0.0079156 | 4.8956 | -0.06467 | 0.17028 | -0.0014568 | 0.0074579 | 0.00043865 | 7.2803e-06 | 8.2304e-05 | -1.7652e-06 | -1.1363e-05 | 85 70 837-AE | -35 | 40 | 20 | - | 0 | 2787.9787 | 2530.2961 | 5.5387 | 1.1018 | 3.7605
NTZ136-1 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 32756.0996 | 1111.25 | -245.038 | 12.2569 | -8.2362 | -1.5842 | 0.037723 | -0.087686 | -0.020791 | 0.0065202 | 4979.2798 | 18.6797 | 88.4117 | -1.1382 | 3.6375 | 0.39256 | -0.0071268 | 0.031294 | 0.00075075 | -0.0070198 | 16.7458 | -0.32573 | 0.43037 | -0.012081 | 0.017815 | 0.0033172 | -9.3458e-05 | 0.00016708 | 3.5834e-05 | -4.3696e-05 | 85 70 805-AE | -35 | 40 | 20 | - | 0 | 3739.1398 | 3350.9753 | 18.3189 | 1.1158 | 3.8083
NTZ136-3 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 32756.0996 | 1111.25 | -245.038 | 12.2569 | -8.2362 | -1.5842 | 0.037723 | -0.087686 | -0.020791 | 0.0065202 | 4979.2798 | 18.6797 | 88.4117 | -1.1382 | 3.6375 | 0.39256 | -0.0071268 | 0.031294 | 0.00075075 | -0.0070198 | 10.1762 | -0.19794 | 0.26153 | -0.0073413 | 0.010826 | 0.0020158 | -5.6793e-05 | 0.00010153 | 2.1776e-05 | -2.6554e-05 | 0 | -35 | 40 | 20 | - | 0 | 3739.1398 | 3350.9753 | 11.1321 | 1.1158 | 3.8083
NTZ136-4 |  | R404A | 50 | 2900 | ACP | 20 | - | 0 | 28653.3008 | 987.749 | -252.849 | 11.321 | -8.1045 | -0.79737 | 0.037694 | -0.078924 | -0.010175 | 0.0036241 | -1271.4399 | -171.71 | 303.185 | -3.1745 | 7.1368 | -3.5683 | -0.0095051 | 0.053512 | -0.023629 | 0.01979 | 5.6419 | 0.0091634 | 0.15374 | -0.00097666 | 0.0024856 | -0.00044399 | -1.1835e-05 | 1.3362e-05 | 2.1551e-05 | 9.5166e-07 | 85 70 664-A | -35 | 40 | 20 | - | 0 | 3225.2539 | 2895.7381 | 6.1003 | 1.1138 | 3.8013
NTZ136-4 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 32756.0996 | 1111.25 | -245.038 | 12.2569 | -8.2362 | -1.5842 | 0.037723 | -0.087686 | -0.020791 | 0.0065202 | 4979.2798 | 18.6797 | 88.4117 | -1.1382 | 3.6375 | 0.39256 | -0.0071268 | 0.031294 | 0.00075075 | -0.0070198 | 5.184 | -0.10084 | 0.13323 | -0.0037399 | 0.005515 | 0.0010269 | -2.8931e-05 | 5.1723e-05 | 1.1093e-05 | -1.3527e-05 | 85 70 616-A | -35 | 40 | 20 | - | 0 | 3739.1398 | 3350.9753 | 5.671 | 1.1158 | 3.8083
NTZ136-9 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 32756.0996 | 1111.25 | -245.038 | 12.2569 | -8.2362 | -1.5842 | 0.037723 | -0.087686 | -0.020791 | 0.0065202 | 4979.2798 | 18.6797 | 88.4117 | -1.1382 | 3.6375 | 0.39256 | -0.0071268 | 0.031294 | 0.00075075 | -0.0070198 | 6.3763 | -0.12403 | 0.16387 | -0.0046 | 0.0067835 | 0.0012631 | -3.5586e-05 | 6.3619e-05 | 1.3645e-05 | -1.6638e-05 | 85 70 838-AE | -35 | 40 | 20 | - | 0 | 3739.1398 | 3350.9753 | 6.9753 | 1.1158 | 3.8083
NTZ215-3 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 42845.3298 | 1509.3143 | -69.1965 | 17.3593 | -7.5936 | -6.6988 | 0.054574 | -0.1152 | -0.066532 | 0.026065 | -3343.7541 | -404.0497 | 426.3081 | -7.5441 | 13.0488 | -1.7761 | -0.037052 | 0.094104 | -0.029786 | -0.0073462 | 51.6607 | 1.6547 | -1.0984 | 0.024598 | -0.034535 | 0.022814 | 0.00012382 | -0.00033099 | 0.0003299 | -0.00012766 | 0 | -35 | 40 | 20 | - | 0 | 5839.1775 | 4896.2591 | 16.6225 | 1.1926 | 4.0702
NTZ215-4 |  | R404A | 50 | 2900 | ACP | 20 | - | 0 | 36376.2243 | 1235.1005 | -83.9045 | 14.4057 | -4.9835 | -4.8381 | 0.04982 | -0.085064 | -0.063924 | 0.015591 | -676.3901 | -224.9305 | 277.7409 | -4.9436 | 7.7311 | -0.58069 | -0.029525 | 0.055961 | -0.0033838 | -0.0085827 | 23.3759 | 0.74874 | -0.497 | 0.01113 | -0.015627 | 0.010323 | 5.6026e-05 | -0.00014977 | 0.00014927 | -5.7763e-05 | 85 70 665-BE | -35 | 40 | 20 | - | 0 | 4947.7053 | 4145.5093 | 7.5215 | 1.1935 | 4.0734
NTZ215-4 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 42845.3298 | 1509.3143 | -69.1965 | 17.3593 | -7.5936 | -6.6988 | 0.054574 | -0.1152 | -0.066532 | 0.026065 | -3343.7541 | -404.0497 | 426.3081 | -7.5441 | 13.0488 | -1.7761 | -0.037052 | 0.094104 | -0.029786 | -0.0073462 | 23.3759 | 0.74874 | -0.497 | 0.01113 | -0.015627 | 0.010323 | 5.6026e-05 | -0.00014977 | 0.00014927 | -5.7763e-05 | 85 70 618-AE | -35 | 40 | 20 | - | 0 | 5839.1775 | 4896.2591 | 7.5215 | 1.1926 | 4.0702
NTZ215-9 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 42845.3298 | 1509.3143 | -69.1965 | 17.3593 | -7.5936 | -6.6988 | 0.054574 | -0.1152 | -0.066532 | 0.026065 | -3343.7541 | -404.0497 | 426.3081 | -7.5441 | 13.0488 | -1.7761 | -0.037052 | 0.094104 | -0.029786 | -0.0073462 | 32.4691 | 1.04 | -0.69034 | 0.01546 | -0.021705 | 0.014339 | 7.782e-05 | -0.00020803 | 0.00020734 | -8.0233e-05 | 85 70 839-AE | -35 | 40 | 20 | - | 0 | 5839.1775 | 4896.2591 | 10.4473 | 1.1926 | 4.0702
NTZ271-3 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 63811.6851 | 2233.3034 | -381.3843 | 25.2048 | -16.6827 | -4.988 | 0.075938 | -0.19153 | -0.055287 | 0.017348 | 7614.4455 | 38.4098 | 169.3371 | -1.1982 | 4.1876 | 0.65828 | -0.0039447 | 0.025291 | 0.016691 | -0.0094511 | 24.6058 | -0.39351 | 0.02658 | -0.017506 | 0.018307 | 0.012506 | -0.00012728 | 0.00023214 | 4.9473e-05 | -0.00010109 | 0 | -35 | 40 | 20 | - | 0 | 8207.2236 | 6635.2988 | 19.9696 | 1.2369 | 4.2215
NTZ271-4 |  | R404A | 50 | 2900 | ACP | 20 | - | 0 | 53958.9162 | 1819.7268 | -355.7212 | 20.1053 | -12.8262 | -3.3007 | 0.062984 | -0.13945 | -0.045185 | 0.0097914 | 5762.6598 | 21.1145 | 182.4292 | -1.2943 | 3.973 | -0.079476 | -0.0088382 | 0.018989 | 0.0070252 | -0.0055474 | 11.8926 | -0.19019 | 0.012847 | -0.008461 | 0.008848 | 0.0060445 | -6.1516e-05 | 0.0001122 | 2.3911e-05 | -4.8858e-05 | 85 70 666-BE | -35 | 40 | 20 | - | 0 | 6967.9445 | 5606.9714 | 9.6518 | 1.2427 | 4.2414
NTZ271-4 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 63811.6851 | 2233.3034 | -381.3843 | 25.2048 | -16.6827 | -4.988 | 0.075938 | -0.19153 | -0.055287 | 0.017348 | 7614.4455 | 38.4098 | 169.3371 | -1.1982 | 4.1876 | 0.65828 | -0.0039447 | 0.025291 | 0.016691 | -0.0094511 | 11.8926 | -0.19019 | 0.012847 | -0.008461 | 0.008848 | 0.0060445 | -6.1516e-05 | 0.0001122 | 2.3911e-05 | -4.8858e-05 | 85 70 620-AE | -35 | 40 | 20 | - | 0 | 8207.2236 | 6635.2988 | 9.6518 | 1.2369 | 4.2215
NTZ271-9 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 63811.6851 | 2233.3034 | -381.3843 | 25.2048 | -16.6827 | -4.988 | 0.075938 | -0.19153 | -0.055287 | 0.017348 | 7614.4455 | 38.4098 | 169.3371 | -1.1982 | 4.1876 | 0.65828 | -0.0039447 | 0.025291 | 0.016691 | -0.0094511 | 17.2443 | -0.27578 | 0.018628 | -0.012268 | 0.01283 | 0.0087646 | -8.9198e-05 | 0.00016269 | 3.4672e-05 | -7.0844e-05 | 85 70 840-AE | -35 | 40 | 20 | - | 0 | 8207.2236 | 6635.2988 | 13.9952 | 1.2369 | 4.2215
NTZ430T4 |  | R404A | 50 | 2900 | - | 20 | - | 0 | 72752.4485 | 2470.201 | -167.8089 | 28.8113 | -9.967 | -9.6763 | 0.09964 | -0.17013 | -0.12785 | 0.031181 | -1352.7802 | -449.8609 | 555.4818 | -9.8871 | 15.4621 | -1.1614 | -0.05905 | 0.11192 | -0.0067676 | -0.017165 | 46.7518 | 1.4975 | -0.99401 | 0.02226 | -0.031253 | 0.020646 | 0.00011205 | -0.00029954 | 0.00029855 | -0.00011553 | 0 | -35 | 40 | 20 | - | 0 | 9895.4106 | 8291.0185 | 15.043 | 1.1935 | 4.0734
NTZ430T4 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 85690.6597 | 3018.6287 | -138.393 | 34.7187 | -15.1872 | -13.3976 | 0.10915 | -0.23039 | -0.13306 | 0.052131 | -6687.5083 | -808.0994 | 852.6161 | -15.0881 | 26.0976 | -3.5523 | -0.074104 | 0.18821 | -0.059572 | -0.014692 | 46.7518 | 1.4975 | -0.99401 | 0.02226 | -0.031253 | 0.020646 | 0.00011205 | -0.00029954 | 0.00029855 | -0.00011553 | 0 | -35 | 40 | 20 | - | 0 | 11678.355 | 9792.5181 | 15.043 | 1.1926 | 4.0702
NTZ542T4 |  | R404A | 50 | 2900 | - | 20 | - | 0 | 107917.8323 | 3639.4536 | -711.4424 | 40.2107 | -25.6523 | -6.6013 | 0.12597 | -0.27889 | -0.090369 | 0.019583 | 11525.3195 | 42.2289 | 364.8585 | -2.5885 | 7.9459 | -0.15895 | -0.017676 | 0.037977 | 0.01405 | -0.011095 | 23.7852 | -0.38038 | 0.025693 | -0.016922 | 0.017696 | 0.012089 | -0.00012303 | 0.0002244 | 4.7823e-05 | -9.7715e-05 | 0 | -35 | 40 | 20 | - | 0 | 13935.8889 | 11213.9427 | 19.3037 | 1.2427 | 4.2414
NTZ542T4 |  | R404A | 60 | 3500 | - | 20 | - | 0 | 127623.3702 | 4466.6068 | -762.7685 | 50.4096 | -33.3654 | -9.976 | 0.15188 | -0.38305 | -0.11057 | 0.034695 | 15228.891 | 76.8197 | 338.6742 | -2.3963 | 8.3751 | 1.3166 | -0.0078895 | 0.050582 | 0.033383 | -0.018902 | 23.7852 | -0.38038 | 0.025693 | -0.016922 | 0.017696 | 0.012089 | -0.00012303 | 0.0002244 | 4.7823e-05 | -9.7715e-05 | 0 | -35 | 40 | 20 | - | 0 | 16414.4473 | 13270.5975 | 19.3037 | 1.2369 | 4.2215

## °F
Model | Drive | Refrigerant | Frequency | Speed | Asercom | RgtBase | ShBase | ScBase | Q0 | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | Q9 | P0 | P1 | P2 | P3 | P4 | P5 | P6 | P7 | P8 | P9 | A0 | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | A9 | version | T. evap | T. cond | RGT | SH | SC | Capacity | Power input | Current | C.O.P. | E.E.R.
|  |  | Hz | rpm |  | °F | °F | °F | Cooling capacity in Btu/h | [9 empty] | Power input in W | [9 empty] | Current consumption in A | [10 empty] | °F | °F | °F | °F | °F | Btu/h | W | A | W/W | Btu/W.h
NTZ048-1 |  | R404A | 60 |  | - | 68 | - | 0 | 24096.8445 | 609.9677 | -80.2297 | 4.8529 | -2.6105 | -0.52784 | 0.0074588 | -0.022704 | -0.0022096 | 0.0014632 | 26.5483 | -42.8643 | 26.6033 | -0.6685 | 0.79218 | -0.071591 | -0.0024467 | 0.0044393 | -0.0014066 | -0.0001418 | 10.5486 | 0.11679 | -0.13957 | 0.0013282 | -0.0019327 | 0.0017832 | 9.9773e-06 | -9.5282e-06 | 1.5369e-05 | -6.018e-06 |  | -25 | 105 | 68 | - | 0 | 5186.1822 | 1158.0469 | 6.553 | 1.3122 | 4.4784
NTZ048-3 |  | R404A | 60 |  | - | 68 | - | 0 | 22961.6596 | 585.9583 | -59.8466 | 4.7015 | -2.3067 | -0.66541 | 0.0073175 | -0.021578 | -0.0032689 | 0.0017835 | 1223.2316 | -22.0774 | -6.0214 | -0.48625 | 0.43164 | 0.23572 | -0.0021768 | 0.0022768 | 4.3179e-06 | -0.0010742 | 6.9397 | 0.076837 | -0.091809 | 0.00087384 | -0.0012716 | 0.001173 | 6.5645e-06 | -6.2683e-06 | 1.0112e-05 | -3.9589e-06 |  | -25 | 105 | 68 | - | 0 | 5121.3908 | 1243.4915 | 4.3114 | 1.2067 | 4.1186
NTZ048-4 |  | R404A | 50 |  | ACP | 68 | - | 0 | 20226.9399 | 519.721 | -76.0611 | 4.1165 | -2.4299 | -0.35063 | 0.0060128 | -0.02023 | -0.00094421 | 0.00095709 | 210.1213 | -29.9844 | 17.1367 | -0.4732 | 0.58771 | 0.0014666 | -0.0017929 | 0.0029704 | -0.00093092 | -0.00033999 | 1.6338 | -0.026467 | 0.010924 | -0.00043594 | 0.00059201 | 6.703e-05 | -1.9106e-06 | 3.911e-06 | -6.232e-07 | -5.053e-07 |  | -25 | 105 | 68 | - | 0 | 4279.8101 | 1022.724 | 2.2284 | 1.2261 | 4.1847
NTZ048-4 |  | R404A | 60 |  | - | 68 | - | 0 | 22961.6596 | 585.9583 | -59.8466 | 4.7015 | -2.3067 | -0.66541 | 0.0073175 | -0.021578 | -0.0032689 | 0.0017835 | 1223.2316 | -22.0774 | -6.0214 | -0.48625 | 0.43164 | 0.23572 | -0.0021768 | 0.0022768 | 4.3179e-06 | -0.0010742 | 3.4785 | 0.038515 | -0.04602 | 0.00043801 | -0.00063738 | 0.00058798 | 3.2905e-06 | -3.142e-06 | 5.0687e-06 | -1.9844e-06 |  | -25 | 105 | 68 | - | 0 | 5121.3908 | 1243.4915 | 2.1611 | 1.2067 | 4.1186
NTZ048-5 |  | R404A | 50 |  | - | 68 | - | 0 | 18875.1896 | 498.2523 | -35.903 | 4.2854 | -1.8335 | -0.67256 | 0.0063994 | -0.019996 | -0.0034093 | 0.0016766 | 376.9964 | -13.3005 | 18.9915 | -0.078295 | 0.40324 | -0.071633 | 0.00080136 | 0.00094611 | -0.00080138 | 1.9833e-05 | -13.8744 | -0.16807 | 0.50302 | -0.0020958 | 0.0035633 | -0.004032 | -6.7307e-06 | 1.9578e-05 | -1.0322e-05 | 1.0904e-05 |  | -25 | 105 | 68 | - | 0 | 4193.8668 | 1099.8205 | 4.8861 | 1.1173 | 3.8132
NTZ048-9 |  | R404A | 60 |  | - | 68 | - | 0 | 22961.6596 | 585.9583 | -59.8466 | 4.7015 | -2.3067 | -0.66541 | 0.0073175 | -0.021578 | -0.0032689 | 0.0017835 | 1223.2316 | -22.0774 | -6.0214 | -0.48625 | 0.43164 | 0.23572 | -0.0021768 | 0.0022768 | 4.3179e-06 | -0.0010742 | 4.3482 | 0.048144 | -0.057525 | 0.00054752 | -0.00079672 | 0.00073498 | 4.1131e-06 | -3.9275e-06 | 6.3358e-06 | -2.4805e-06 |  | -25 | 105 | 68 | - | 0 | 5121.3908 | 1243.4915 | 2.7014 | 1.2067 | 4.1186
NTZ068-1 |  | R404A | 60 |  | - | 68 | - | 0 | 52465.2538 | 1096.7058 | -519.9388 | 8.6131 | -7.5962 | 2.002 | 0.020775 | -0.037953 | 0.012759 | -0.0033974 | -191.6648 | 25.4034 | 59.6722 | 0.30311 | 0.10878 | -0.4274 | 0.0018065 | -0.00056839 | 0.00021377 | 0.0011502 | 8.2555 | -0.045744 | 0.0034978 | -0.001268 | 0.0017608 | 0.00042973 | -5.0728e-06 | 1.5874e-05 | -1.9504e-06 | -1.88e-06 |  | -25 | 105 | 68 | - | 0 | 7584.1886 | 1837.6721 | 8.5719 | 1.2092 | 4.1271
NTZ068-3 |  | R404A | 60 |  | - | 68 | - | 0 | 48185.4359 | 972.953 | -398.0033 | 6.8786 | -5.5982 | 1.2292 | 0.01141 | -0.032013 | 0.0050615 | -0.0020459 | 1479.5475 | 13.0039 | 11.1575 | 0.0095121 | 0.081233 | 0.024066 | 0.00063074 | 0.00078312 | 0.0013357 | -5.9905e-05 | 9.763 | 0.12095 | -0.1006 | 0.0010417 | -0.0018369 | 0.0012498 | 6.6358e-06 | -5.5956e-06 | 1.3408e-05 | -3.8007e-06 |  | -25 | 105 | 68 | - | 0 | 8575.4865 | 1988.0477 | 6.8618 | 1.2639 | 4.3135
NTZ068-4 |  | R404A | 50 |  | ACP | 68 | - | 0 | 40835.1152 | 824.5364 | -337.2909 | 5.8293 | -4.7443 | 1.0417 | 0.0096693 | -0.02713 | 0.0042894 | -0.0017338 | 1253.8538 | 11.0202 | 9.4555 | 0.0080611 | 0.068841 | 0.020394 | 0.00053453 | 0.00066366 | 0.001132 | -5.0767e-05 | 5.1656 | 0.063995 | -0.053229 | 0.00055116 | -0.00097191 | 0.00066128 | 3.511e-06 | -2.9606e-06 | 7.0942e-06 | -2.011e-06 |  | -25 | 105 | 68 | - | 0 | 7267.3614 | 1684.7862 | 3.6306 | 1.2639 | 4.3135
NTZ068-4 |  | R404A | 60 |  | - | 68 | - | 0 | 48185.4359 | 972.953 | -398.0033 | 6.8786 | -5.5982 | 1.2292 | 0.01141 | -0.032013 | 0.0050615 | -0.0020459 | 1479.5475 | 13.0039 | 11.1575 | 0.0095121 | 0.081233 | 0.024066 | 0.00063074 | 0.00078312 | 0.0013357 | -5.9905e-05 | 5.1656 | 0.063995 | -0.053229 | 0.00055116 | -0.00097191 | 0.00066128 | 3.511e-06 | -2.9606e-06 | 7.0942e-06 | -2.011e-06 |  | -25 | 105 | 68 | - | 0 | 8575.4865 | 1988.0477 | 3.6306 | 1.2639 | 4.3135
NTZ068-5 |  | R404A | 50 |  | - | 68 | - | 0 | 34554.4637 | 850.59 | -234.1589 | 6.921 | -5.0767 | 0.54958 | 0.012206 | -0.034367 | 0.0043872 | -0.0013632 | 1006.2543 | -8.6968 | 18.8137 | -0.26507 | 0.45335 | -0.064864 | -0.00091133 | 0.0040431 | -0.00057707 | 0.00017442 | 10.7842 | -0.13975 | -0.044445 | -0.0036722 | 0.003204 | 0.00080644 | -3.9004e-06 | 4.5858e-05 | -5.5378e-06 | -2.4003e-06 |  | -25 | 105 | 68 | - | 0 | 7180.9527 | 1768.8016 | 9.6145 | 1.1895 | 4.0598
NTZ068-9 |  | R404A | 60 |  | - | 68 | - | 0 | 48185.4359 | 972.953 | -398.0033 | 6.8786 | -5.5982 | 1.2292 | 0.01141 | -0.032013 | 0.0050615 | -0.0020459 | 1479.5475 | 13.0039 | 11.1575 | 0.0095121 | 0.081233 | 0.024066 | 0.00063074 | 0.00078312 | 0.0013357 | -5.9905e-05 | 6.5087 | 0.080634 | -0.067068 | 0.00069446 | -0.0012246 | 0.00083321 | 4.4239e-06 | -3.7304e-06 | 8.9387e-06 | -2.5338e-06 |  | -25 | 105 | 68 | - | 0 | 8575.4865 | 1988.0477 | 4.5746 | 1.2639 | 4.3135
NTZ096-1 |  | R404A | 60 |  | - | 68 | - | 0 | 37043.0739 | 907.0838 | 106.0794 | 7.7415 | -0.80021 | -3.0086 | 0.015623 | -0.025267 | -0.015857 | 0.0075154 | 231.6101 | -114.8466 | 39.9093 | -1.3933 | 1.9653 | 0.10962 | -0.0037806 | 0.010503 | -0.0032219 | -0.0013267 | 19.9138 | 0.28016 | -0.23952 | 0.00091107 | -0.0042764 | 0.0035353 | -4.2188e-07 | -9.0573e-06 | 3.5526e-05 | -1.3023e-05 |  | -25 | 105 | 68 | - | 0 | 10441.8821 | 2572.7091 | 13.0763 | 1.1892 | 4.0587
NTZ096-3 |  | R404A | 60 |  | - | 68 | - | 0 | 41824.2089 | 1010.3246 | -5.2005 | 8.3197 | -2.4524 | -2.1885 | 0.015665 | -0.030646 | -0.0096233 | 0.005585 | -381.4818 | -98.6652 | 54.6237 | -1.3148 | 1.6704 | -0.06572 | -0.0038141 | 0.0097415 | -0.0022719 | -0.00069862 | 11.9693 | 0.16839 | -0.14392 | 0.00054742 | -0.0025703 | 0.0021247 | -2.5338e-07 | -5.4425e-06 | 2.1356e-05 | -7.8273e-06 |  | -25 | 105 | 68 | - | 0 | 10390.6146 | 2405.9388 | 7.8619 | 1.2654 | 4.3187
NTZ096-4 |  | R404A | 50 |  | ACP | 68 | - | 0 | 28800.1744 | 858.1509 | 118.5755 | 8.4195 | -1.3382 | -2.6726 | 0.02007 | -0.02769 | -0.014621 | 0.0064614 | -1791.1328 | -95.4943 | 86.2024 | -0.88225 | 1.8417 | -0.42676 | -0.0010472 | 0.0086336 | -0.0046424 | 0.00048885 | 2.0582 | -0.050613 | 0.040197 | -0.0012681 | 0.0012481 | -5.0658e-05 | -6.02e-06 | 1.2284e-05 | -1.0852e-06 | -4.3991e-07 |  | -25 | 105 | 68 | - | 0 | 8485.2322 | 1985.0904 | 3.6068 | 1.2524 | 4.2745
NTZ096-4 |  | R404A | 60 |  | - | 68 | - | 0 | 41824.2089 | 1010.3246 | -5.2005 | 8.3197 | -2.4524 | -2.1885 | 0.015665 | -0.030646 | -0.0096233 | 0.005585 | -381.4818 | -98.6652 | 54.6237 | -1.3148 | 1.6704 | -0.06572 | -0.0038141 | 0.0097415 | -0.0022719 | -0.00069862 | 5.5775 | 0.078466 | -0.067064 | 0.00025509 | -0.0011977 | 0.00099009 | -1.1807e-07 | -2.5361e-06 | 9.9516e-06 | -3.6474e-06 |  | -25 | 105 | 68 | - | 0 | 10390.6146 | 2405.9388 | 3.6635 | 1.2654 | 4.3187
NTZ108-1 |  | R404A | 60 |  | - | 68 | - | 0 | 48932.357 | 1516.0577 | -42.9107 | 13.6519 | -6.2196 | -1.8763 | 0.02319 | -0.064821 | -0.0075926 | 0.0035841 | 687.9794 | -24.478 | 52.629 | -0.31951 | 0.99557 | -0.12076 | -0.00010972 | 0.0045437 | -0.0013554 | -0.00030814 | 12.1227 | -0.12689 | 0.052874 | -0.0026779 | 0.0037187 | 0.00087011 | 3.2729e-06 | 3.7011e-05 | -7.9278e-07 | -5.1074e-06 |  | -25 | 105 | 68 | - | 0 | 12323.7621 | 2998.2956 | 15.6881 | 1.2043 | 4.1103
NTZ108-3 |  | R404A | 60 |  | - | 68 | - | 0 | 48388.5781 | 1498.0421 | -57.4035 | 13.4783 | -6.3493 | -1.7098 | 0.022899 | -0.064599 | -0.0064573 | 0.0031819 | -2667.6295 | -89.381 | 132.2442 | -0.92484 | 2.0317 | -0.76091 | -0.0031432 | 0.0090972 | -0.005407 | 0.0013573 | 6.9471 | -0.072691 | 0.03023 | -0.0015341 | 0.0021304 | 0.00049899 | 1.8756e-06 | 2.1203e-05 | -4.5474e-07 | -2.9274e-06 |  | -25 | 105 | 68 | - | 0 | 12017.1631 | 2860.0317 | 8.9874 | 1.2311 | 4.2018
NTZ108-4 |  | R404A | 50 |  | ACP | 68 | - | 0 | 47227.7328 | 1179.5427 | -179.4217 | 10.0485 | -5.117 | -0.70764 | 0.016124 | -0.04749 | -0.0036358 | 0.0017064 | 1002.5393 | -11.741 | 29.3945 | -0.28755 | 0.45474 | -0.0055862 | -0.00030775 | 0.0022468 | 0.00079083 | -0.00045359 | 4.4437 | -0.090412 | 0.0029867 | -0.0016665 | 0.0019345 | 0.00028367 | -5.9906e-06 | 1.6344e-05 | -4.4681e-06 | -1.3911e-06 |  | -25 | 105 | 68 | - | 0 | 10419.5413 | 2356.681 | 4.813 | 1.2954 | 4.4213
NTZ108-4 |  | R404A | 60 |  | - | 68 | - | 0 | 48388.5781 | 1498.0421 | -57.4035 | 13.4783 | -6.3493 | -1.7098 | 0.022899 | -0.064599 | -0.0064573 | 0.0031819 | -2667.6295 | -89.381 | 132.2442 | -0.92484 | 2.0317 | -0.76091 | -0.0031432 | 0.0090972 | -0.005407 | 0.0013573 | 3.7593 | -0.039335 | 0.016358 | -0.00083014 | 0.0011528 | 0.00027002 | 1.0149e-06 | 1.1474e-05 | -2.4607e-07 | -1.5841e-06 |  | -25 | 105 | 68 | - | 0 | 12017.1631 | 2860.0317 | 4.8633 | 1.2311 | 4.2018
NTZ108-9 |  | R404A | 60 |  | - | 68 | - | 0 | 48388.5781 | 1498.0421 | -57.4035 | 13.4783 | -6.3493 | -1.7098 | 0.022899 | -0.064599 | -0.0064573 | 0.0031819 | -2667.6295 | -89.381 | 132.2442 | -0.92484 | 2.0317 | -0.76091 | -0.0031432 | 0.0090972 | -0.005407 | 0.0013573 | 4.6239 | -0.048382 | 0.02012 | -0.0010211 | 0.001418 | 0.00033212 | 1.2483e-06 | 1.4113e-05 | -3.0267e-07 | -1.9484e-06 |  | -25 | 105 | 68 | - | 0 | 12017.1631 | 2860.0317 | 5.9819 | 1.2311 | 4.2018
NTZ136-1 |  | R404A | 60 |  | - | 68 | - | 0 | 63098.1513 | 1508.6079 | -145.9321 | 12.434 | -4.613 | -1.6457 | 0.022076 | -0.051315 | -0.012167 | 0.0038157 | 3888.8485 | 4.3011 | 7.4982 | -0.40568 | 0.77103 | 0.23259 | -0.001222 | 0.0053658 | 0.00012873 | -0.0012037 | 17.3769 | -0.10254 | 0.01652 | -0.003107 | 0.0032717 | 0.0015465 | -1.6025e-05 | 2.8649e-05 | 6.1444e-06 | -7.4925e-06 |  | -25 | 105 | 68 | - | 0 | 15855.104 | 3797.8306 | 19.9581 | 1.2232 | 4.1748
NTZ136-3 |  | R404A | 60 |  | - | 68 | - | 0 | 63098.1513 | 1508.6079 | -145.9321 | 12.434 | -4.613 | -1.6457 | 0.022076 | -0.051315 | -0.012167 | 0.0038157 | 3888.8485 | 4.3011 | 7.4982 | -0.40568 | 0.77103 | 0.23259 | -0.001222 | 0.0053658 | 0.00012873 | -0.0012037 | 10.5596 | -0.062314 | 0.010039 | -0.0018881 | 0.0019882 | 0.00093977 | -9.7381e-06 | 1.7409e-05 | 3.7338e-06 | -4.5531e-06 |  | -25 | 105 | 68 | - | 0 | 15855.104 | 3797.8306 | 12.1282 | 1.2232 | 4.1748
NTZ136-4 |  | R404A | 50 |  | ACP | 68 | - | 0 | 56728.4169 | 1349.9077 | -205.4542 | 11.2857 | -5.2001 | -0.853 | 0.022059 | -0.046187 | -0.0059546 | 0.0021209 | -3709.9473 | -93.5393 | 179.9572 | -1.1169 | 1.8748 | -1.2974 | -0.0016298 | 0.0091757 | -0.0040516 | 0.0033933 | 2.9474 | 0.0020763 | 0.080047 | -0.00017994 | 0.00038402 | -0.00027095 | -2.0293e-06 | 2.2911e-06 | 3.6954e-06 | 1.6318e-07 |  | -25 | 105 | 68 | - | 0 | 13428.3022 | 3272.9858 | 6.5451 | 1.2021 | 4.1028
NTZ136-4 |  | R404A | 60 |  | - | 68 | - | 0 | 63098.1513 | 1508.6079 | -145.9321 | 12.434 | -4.613 | -1.6457 | 0.022076 | -0.051315 | -0.012167 | 0.0038157 | 3888.8485 | 4.3011 | 7.4982 | -0.40568 | 0.77103 | 0.23259 | -0.001222 | 0.0053658 | 0.00012873 | -0.0012037 | 5.3793 | -0.031744 | 0.0051139 | -0.00096184 | 0.0010128 | 0.00047874 | -4.9608e-06 | 8.8688e-06 | 1.9021e-06 | -2.3194e-06 |  | -25 | 105 | 68 | - | 0 | 15855.104 | 3797.8306 | 6.1784 | 1.2232 | 4.1748
NTZ136-9 |  | R404A | 60 |  | - | 68 | - | 0 | 63098.1513 | 1508.6079 | -145.9321 | 12.434 | -4.613 | -1.6457 | 0.022076 | -0.051315 | -0.012167 | 0.0038157 | 3888.8485 | 4.3011 | 7.4982 | -0.40568 | 0.77103 | 0.23259 | -0.001222 | 0.0053658 | 0.00012873 | -0.0012037 | 6.6166 | -0.039045 | 0.0062901 | -0.0011831 | 0.0012458 | 0.00058885 | -6.1018e-06 | 1.0909e-05 | 2.3396e-06 | -2.8529e-06 |  | -25 | 105 | 68 | - | 0 | 15855.104 | 3797.8306 | 7.5994 | 1.2232 | 4.1748
NTZ215-3 |  | R404A | 60 |  | - | 68 | - | 0 | 64097.2945 | 1867.64 | 474.4647 | 17.3773 | -1.1927 | -7.2749 | 0.031937 | -0.067414 | -0.038935 | 0.015254 | -2672.968 | -196.0312 | 145.239 | -2.2349 | 3.3216 | -0.26383 | -0.0063533 | 0.016136 | -0.0051073 | -0.0012596 | 45.8678 | 0.7814 | -0.72928 | 0.0073699 | -0.010647 | 0.0073325 | 2.1231e-05 | -5.6755e-05 | 5.6566e-05 | -2.1889e-05 |  | -25 | 105 | 68 | - | 0 | 24478.0365 | 5560.9114 | 18.1671 | 1.2897 | 4.4018
NTZ215-4 |  | R404A | 50 |  | ACP | 68 | - | 0 | 60849.4381 | 1487.9778 | 235.5056 | 13.9688 | 0.3306 | -4.7752 | 0.029155 | -0.049781 | -0.037409 | 0.0091239 | -999.0766 | -100.1618 | 93.5312 | -1.3468 | 1.8092 | -0.019379 | -0.0050625 | 0.0095955 | -0.00058021 | -0.0014717 | 20.7547 | 0.35357 | -0.32999 | 0.0033348 | -0.0048176 | 0.0033179 | 9.6067e-06 | -2.5681e-05 | 2.5596e-05 | -9.9046e-06 |  | -25 | 105 | 68 | - | 0 | 20744.3413 | 4686.3838 | 8.2204 | 1.297 | 4.4265
NTZ215-4 |  | R404A | 60 |  | - | 68 | - | 0 | 64097.2945 | 1867.64 | 474.4647 | 17.3773 | -1.1927 | -7.2749 | 0.031937 | -0.067414 | -0.038935 | 0.015254 | -2672.968 | -196.0312 | 145.239 | -2.2349 | 3.3216 | -0.26383 | -0.0063533 | 0.016136 | -0.0051073 | -0.0012596 | 20.7547 | 0.35357 | -0.32999 | 0.0033348 | -0.0048176 | 0.0033179 | 9.6067e-06 | -2.5681e-05 | 2.5596e-05 | -9.9046e-06 |  | -25 | 105 | 68 | - | 0 | 24478.0365 | 5560.9114 | 8.2204 | 1.2897 | 4.4018
NTZ215-9 |  | R404A | 60 |  | - | 68 | - | 0 | 64097.2945 | 1867.64 | 474.4647 | 17.3773 | -1.1927 | -7.2749 | 0.031937 | -0.067414 | -0.038935 | 0.015254 | -2672.968 | -196.0312 | 145.239 | -2.2349 | 3.3216 | -0.26383 | -0.0063533 | 0.016136 | -0.0051073 | -0.0012596 | 28.8283 | 0.49111 | -0.45836 | 0.004632 | -0.0066916 | 0.0046085 | 1.3344e-05 | -3.5671e-05 | 3.5552e-05 | -1.3757e-05 |  | -25 | 105 | 68 | - | 0 | 24478.0365 | 5560.9114 | 11.4181 | 1.2897 | 4.4018
NTZ271-3 |  | R404A | 60 |  | - | 68 | - | 0 | 112178.3086 | 2971.5169 | 25.6306 | 25.8708 | -8.3292 | -5.1935 | 0.04444 | -0.11208 | -0.032355 | 0.010152 | 4913.3918 | 13.382 | 45.0382 | -0.44364 | 0.83174 | 0.26716 | -0.0006764 | 0.0043366 | 0.002862 | -0.0016206 | 35.0354 | -0.030464 | -0.40819 | -0.0045817 | 0.0025598 | 0.0052524 | -2.1824e-05 | 3.9805e-05 | 8.483e-06 | -1.7333e-05 |  | -25 | 105 | 68 | - | 0 | 33976.5971 | 7423.0229 | 21.8123 | 1.3411 | 4.5772
NTZ271-4 |  | R404A | 50 |  | ACP | 68 | - | 0 | 101768.045 | 2446.3115 | -139.7292 | 20.2516 | -6.5958 | -3.1808 | 0.036859 | -0.081606 | -0.026443 | 0.0057301 | 2900.2498 | 1.3032 | 66.5594 | -0.35817 | 0.94075 | 0.028238 | -0.0015155 | 0.003256 | 0.0012046 | -0.00095119 | 16.9335 | -0.014724 | -0.19729 | -0.0022144 | 0.0012372 | 0.0025386 | -1.0548e-05 | 1.9239e-05 | 4.1e-06 | -8.3775e-06 |  | -25 | 105 | 68 | - | 0 | 28831.9669 | 6278.6141 | 10.5424 | 1.3455 | 4.5921
NTZ271-4 |  | R404A | 60 |  | - | 68 | - | 0 | 112178.3086 | 2971.5169 | 25.6306 | 25.8708 | -8.3292 | -5.1935 | 0.04444 | -0.11208 | -0.032355 | 0.010152 | 4913.3918 | 13.382 | 45.0382 | -0.44364 | 0.83174 | 0.26716 | -0.0006764 | 0.0043366 | 0.002862 | -0.0016206 | 16.9335 | -0.014724 | -0.19729 | -0.0022144 | 0.0012372 | 0.0025386 | -1.0548e-05 | 1.9239e-05 | 4.1e-06 | -8.3775e-06 |  | -25 | 105 | 68 | - | 0 | 33976.5971 | 7423.0229 | 10.5424 | 1.3411 | 4.5772
NTZ271-9 |  | R404A | 60 |  | - | 68 | - | 0 | 112178.3086 | 2971.5169 | 25.6306 | 25.8708 | -8.3292 | -5.1935 | 0.04444 | -0.11208 | -0.032355 | 0.010152 | 4913.3918 | 13.382 | 45.0382 | -0.44364 | 0.83174 | 0.26716 | -0.0006764 | 0.0043366 | 0.002862 | -0.0016206 | 24.5535 | -0.02135 | -0.28607 | -0.0032109 | 0.0017939 | 0.003681 | -1.5295e-05 | 2.7896e-05 | 5.945e-06 | -1.2147e-05 |  | -25 | 105 | 68 | - | 0 | 33976.5971 | 7423.0229 | 15.2865 | 1.3411 | 4.5772
NTZ430T4 |  | R404A | 50 |  | - | 68 | - | 0 | 121698.8762 | 2975.9556 | 471.0112 | 27.9376 | 0.6612 | -9.5505 | 0.058311 | -0.099561 | -0.074818 | 0.018248 | -1998.1532 | -200.3236 | 187.0624 | -2.6937 | 3.6183 | -0.038759 | -0.010125 | 0.019191 | -0.0011604 | -0.0029433 | 41.5094 | 0.70715 | -0.65998 | 0.0066696 | -0.0096352 | 0.0066358 | 1.9213e-05 | -5.1362e-05 | 5.1191e-05 | -1.9809e-05 |  | -25 | 105 | 68 | - | 0 | 41488.6826 | 9372.7676 | 16.4408 | 1.297 | 4.4265
NTZ430T4 |  | R404A | 60 |  | - | 68 | - | 0 | 128194.5889 | 3735.28 | 948.9295 | 34.7546 | -2.3853 | -14.5497 | 0.063875 | -0.13483 | -0.077871 | 0.030508 | -5345.936 | -392.0624 | 290.4779 | -4.4697 | 6.6432 | -0.52767 | -0.012707 | 0.032272 | -0.010215 | -0.0025193 | 41.5094 | 0.70715 | -0.65998 | 0.0066696 | -0.0096352 | 0.0066358 | 1.9213e-05 | -5.1362e-05 | 5.1191e-05 | -1.9809e-05 |  | -25 | 105 | 68 | - | 0 | 48956.0731 | 11121.8228 | 16.4408 | 1.2897 | 4.4018
NTZ542T4 |  | R404A | 50 |  | - | 68 | - | 0 | 203536.09 | 4892.6231 | -279.4584 | 40.5032 | -13.1916 | -6.3616 | 0.073719 | -0.16321 | -0.052885 | 0.01146 | 5800.4996 | 2.6064 | 133.1187 | -0.71635 | 1.8815 | 0.056476 | -0.0030309 | 0.0065119 | 0.0024092 | -0.0019024 | 33.867 | -0.029448 | -0.39457 | -0.0044289 | 0.0024744 | 0.0050773 | -2.1096e-05 | 3.8477e-05 | 8.2001e-06 | -1.6755e-05 |  | -25 | 105 | 68 | - | 0 | 57663.9338 | 12557.2282 | 21.0849 | 1.3455 | 4.5921
NTZ542T4 |  | R404A | 60 |  | - | 68 | - | 0 | 224356.6172 | 5943.0338 | 51.2611 | 51.7416 | -16.6585 | -10.387 | 0.08888 | -0.22417 | -0.064709 | 0.020304 | 9826.7836 | 26.764 | 90.0765 | -0.88729 | 1.6635 | 0.53432 | -0.0013528 | 0.0086732 | 0.0057241 | -0.0032411 | 33.867 | -0.029448 | -0.39457 | -0.0044289 | 0.0024744 | 0.0050773 | -2.1096e-05 | 3.8477e-05 | 8.2001e-06 | -1.6755e-05 |  | -25 | 105 | 68 | - | 0 | 67953.1942 | 14846.0459 | 21.0849 | 1.3411 | 4.5772